## Slide 1: Electrical Service Design of a 9 – Storied Residential Building with Single- and Double-unit Floorplans
A presentation by
1706038 – Asif Billah
1706052 – Nazmus Salehin
1706053 – Saleh Ahmed Khan
1706054 – Tiasa Mondal
1706058 – Abdullah Jubair Bin Iqbal
1706059 – Tasnim Farhan Fatin
1706064 – Sadat Tahmeed Azad
Course: EEE 414
Electrical Service Design

## Slide 2: Our Project
Our designed building plan has been taken from an under construction building in Baridhara residential area, with swimming pool facility on rooftop. We had to make proper adjustments to the initial plan to accommodate 9 residential stories, 6 of which are dual units and 3 single units, and had to add another basement parking area to make room for 15 cars (one for each unit) along with the necessary driving ramp for cars to move between levels. We also had to extend the plan to include substation and emergency generator room. Electric designs were then made according to the theory taught in our EEE 414 course and using practical considerations.

## Slide 3: Design Steps
Layout
Fittings and features
Conduit
Circuit diagrams
Power Distribution & substation

## Slide 4
Floor Layout Basement

## Slide 5
Floor Layout Ground Floor

## Slide 6
Floor Layout Typical 2 Unit

## Slide 7
Floor Layout Typical 1 Unit

## Slide 8
Floor Layout Roof

## Slide 9
Info Table - Fittings and Fixtures
Symbol | Legend | Description | Power Rating
 | LT | Tube Light | 40 W
 | LW | Wall Mounted Light at Lintel Level | 15 W
 | LC | Ceiling Light | 5 W
 | SS/ESB | Switch Board/ Emergency Switch Board | -
 | SDB | Sub Distribution Board | -
 | ESDB | Emergency Sub Distribution Board | -
 | MDB | Main Distribution Board | -
Symbol | Legend | Description | Power Rating
 | SS | 2 Pin Socket at Switchboard Level (5A) | 100 W
 | TV | Television Socket | 150 W
 | Q | 3 Pin Socket (5A/20A) | 4000 W
 | ST | 2 Pin Socket at Skirting Height (5A) | 100 W
 | EMDB | Emergency Main Distribution Board | -
 | F | Ceiling Fan | 100 W
 | E | Exhaust Fan | 40 W

## Slide 10
Fittings and Fixtures Basement

## Slide 11
Fittings and Fixtures Ground

## Slide 12
Fittings and Fixtures Typical 2 Unit

## Slide 13
Fittings and Fixtures Typical 1 Unit

## Slide 14
Fittings and Fixtures Roof

## Slide 15
Conduit Layout
Basement

## Slide 16
Conduit Layout
Ground

## Slide 17
Conduit Layout
Typical 1 Unit

## Slide 18
Conduit Layout
Typical 2 Unit

## Slide 19
Conduit Layout
Roof

## Slide 20
Emergency Conduit Layout
Basement

## Slide 21
Emergency Conduit Layout
Ground

## Slide 22
Emergency Conduit Layout
Typical 2 Floor

## Slide 23
Emergency Conduit Layout
Typical 1 Floor

## Slide 24
Emergency Conduit Layout
Roof

## Slide 25
Conduit Layout of TV, Cable and Data Networks
Symbols | Descriptions
 | TV Dish Line
 | Telephone Line
 | Port For Communication
 | Internet Router

## Slide 26
Conduit Layout of
TV, Cable and
Data Networks
2 Unit

## Slide 27
Conduit Layout of
TV, Cable and
Data Networks
1 Unit

## Slide 28
Lighting Protection System
Calculation
Length of the Building: 72'
Width of the Building: 53'
Total Area = 3816 sq ft, 354.6 sq meters
Conductors on the Roof: (24" conductors, 25' maximum gap)
4 on 4 corners
Along the length 2 more conductors are needed
Gap between each conductor = 24'
Along the width 2 more conductors are needed
Gap between each conductor = 17.67'
Down Conductor:
Perimeter of the Building = 250'
Required Down Conductor = 250/100 = 2.5 ~= 3

## Slide 29
Lighting Protection System
Layout
Roof Conductor
Air Spike
Down Conductor

## Slide 30
Some Notes on Fitting and Fixtures and Conduits
We chose 20W LED bulbs and tubelights (2000 W in standard 100 lumen/W rate).
For power socket, 3 pin Q (20A, 4000W) were used. We tried to distribute 4 power sockets to each of the dual units and 5 to the single unit.
For emergency conduit, only one light and one fan per each bedroom, half of the lights in the garage, the stair lights and some few other lights were kept. Our emergency system is part of the main system and works as a partial backup, so we didn’t add any separate emergency system.

## Slide 35
Switch Board Diagrams

## Slide 36
Switch Board Connection Diagram – Basement

## Slide 37
Switch Board Connection Calculations – Basement

## Slide 38
Switch Board Connection Diagram – Ground Floor

## Slide 39
Switch Board Connection Calculations – Ground Floor

## Slide 40
Switch Board Connection Diagram – Typical 2 Unit

## Slide 41
Switch Board Connection Calculation – Typical 2 Unit

## Slide 42
Switch Board Connection Diagram – Typical 1 Unit

## Slide 43
Switch Board Connection Calculation – Typical 1 Unit

## Slide 44
Switch Board Connection Diagram – Roof

## Slide 45
Switch Board Connection Calculations – Roof

## Slide 46
Emergency Switch Board Diagrams

## Slide 47
Emergency Switch Board Connection Diagram – Basement

## Slide 48
Emergency Switch Board Connection Calculations – Basement

## Slide 49
Emergency Switch Board Connection Diagram – Ground Floor

## Slide 50
Emergency Switch Board Connection Calculations – Ground Floor

## Slide 51
Emergency Switch Board Connection Diagram – Typical 2 Unit

## Slide 52
Emergency Switch Board Connection Diagram – Typical 2 Unit (Unit 1)

## Slide 53
Emergency Switch Board Connection Diagram – Typical 1 Unit

## Slide 54
Emergency Switch Board Connection Diagram – Typical 1 Unit

## Slide 55
Emergency Switch Board Connection Diagram – Roof

## Slide 56
Emergency Switch Board Connection Calculations – Roof

## Slide 57
Sub Distribution Board Diagrams

## Slide 58
SDB Diagram – Basement

## Slide 59
SDB Calculations - Basement
Calculation:
For SDB_U, we notice that all switchboards are below 5A rating (similarly for the emergency case, as load is even lesser). Thus, standard 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used for connecting switchboards to SDBs, along with 5A MCB breakers.
We assume utility factor for normal load to be 0.7, assuming they would be operating 70% of the time. Power Factor = 0.9
SDB_U:
Load = 0.7 x total load = 0.7 x 880 = 616W (No power sockets are present here) Current = 616/(220 x 0.9) = 3.11 A Thus, 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used, along with 5A MCCB breaker, to connect it to the MDB.

## Slide 60
SDB Diagram – Ground Floor

## Slide 61
SDB Calculations – Ground Floor
Calculation:
For SDB_G, we notice that all switchboards are below 5A rating (similarly for the emergency case, as load is even lesser). Thus, standard 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used for connecting switchboards to SDBs, along with 5A MCB breakers.
We assume utility factor for normal load to be 0.7, assuming they would be operating 70% of the time. Power Factor = 0.9
SDB_G:
Load = 0.7 x total load = 0.7 x 1040 = 728W (No power sockets are present here) Current = 728/(220 x 0.9) = 3.677 A Thus, 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used, along with 5A SP MCCB breaker, to connect it to the MDB.

## Slide 62
SDB Diagram – Single Unit

## Slide 63
SDB Calculation – Single Unit
For SDB_U1, we notice that all switchboards are below 5A rating (similarly for the emergency case, as load is even lesser). Thus, standard 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used for connecting switchboards to SDBs, along with 5A MCB breakers.
Here, power sockets with rating 20A and 4000W are present. (4000V/220A = 18.18A). Thus, we have used 20A SP MCB Breakers and 2x6 rm BYM + 6 rm BYA ECC wires.
We assume utility factor for normal load to be 0.7, assuming they would be operating 70% of the time.
For a typical AC, watt rating is 1500 Watt. As our power socket is 4000W, the ratio is then 1500/4000 = 0.375. But an AC will not run all the time. If we assume it runs 80% of the time during summer, then our utility factor should be 0.8x0.375 = 0.3. Thus for power sockets, we assume utility factor to be 30%.
Here, power factor = 0.9
SDB_U1:
Load = 0.7 x total load + 0.4 x power socket load = 0.7 x 3520 + 0.3 x 4000 x 5 = 8464W (5 Q sockets are present) Current = 8464/(220 x 0.9) = 42.75 A Thus, 2 x 25 rm BYM cables and 25 rm BYA ECC cable has been used, along with 50A SP MCCB breaker, to connect it to the MDB.

## Slide 64
SDB Diagram – Double Unit – Unit 1

## Slide 65
SDB Calculation – Double Unit – Unit 1
Calculation:
For SDB1_U2, we notice that all switchboards are below 5A rating (similarly for the emergency case, as load is even lesser). Thus, standard 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used for connecting switchboards to SDBs, along with 5A MCB breakers.
Here, power sockets with rating 20A and 4000W are present. (4000V/220A = 18.18A). Thus, we have used 20A SP MCB Breakers and 2x6 rm BYM + 6 rm BYA ECC wires.
We assume utility factor for normal load to be 0.7, assuming they would be operating 70% of the time. And for power sockets, we assume utility factor to be 30%.
Here, power factor = 0.9
SDB1_U2:
Load = 0.7 x total load + 0.9 x power socket load = 0.7 x 2110 + 0.3 x 4000 x 4 = 6277W (4 Q sockets are present) Current = 6277/(220 x 0.9) = 31.7 A Thus, 2 x 16 rm BYM cables and 16 rm BYA ECC cable has been used, along with 40A SP MCCB breaker, to connect it to the MDB.

## Slide 66
SDB Diagram – Double Unit – Unit 2

## Slide 67
SDB Calculation – Double Unit – Unit 2
Calculation:
For SDB2_U2, we notice that all switchboards are below 5A rating (similarly for the emergency case, as load is even lesser). Thus, standard 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used for connecting switchboards to SDBs, along with 5A MCB breakers.
Here, power sockets with rating 20A and 4000W are present. (4000V/220A = 18.18A). Thus, we have used 20A SP MCB Breakers and 2x6 rm BYM + 6 rm BYA ECC wires.
We assume utility factor for normal load to be 0.7, assuming they would be operating 70% of the time. And for power sockets, we assume utility factor to be 40%.
Here, power factor = 0.9
SDB2_U2:
Load = 0.7 x total load + 0.9 x power socket load = 0.7 x 1850 + 0.4 x 4000 x 4 = 6095W (4 Q sockets are present) Current = 7695/(220 x 0.9) = 30.78 A Thus, 2 x 16 rm BYM cables and 16 rm BYA ECC cable has been used, along with 40A SP MCCB breaker, to connect it to the MDB.

## Slide 68
SDB Diagram – Roof

## Slide 69
SDB Calculation – Roof
Calculation:
For SDB_R, we notice that all switchboards are below 5A rating (similarly for the emergency case, as load is even lesser). Thus, standard 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used for connecting switchboards to SDBs, along with 5A MCB breakers.
We assume utility factor for normal load to be 0.7, assuming they would be operating 70% of the time. Power Factor = 0.9
SDB_R:
Load = 0.7 x total load = 0.7 x 250 = 175W (No power sockets are present here) Current = 175/(220 x 0.9) = 0.88 A Thus, 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used, along with 5A SP MCCB breaker, to connect it to the MDB.

## Slide 70
Emergency Sub Distribution Board Diagrams

## Slide 71
ESDB Diagram – Basement

## Slide 72
ESDB Calculations - Basement
ESDB_U:
Emergency Load = 0.7 x total emergency load = 0.7 x 540 = 378W Current = 616/(220 x 0.9) = 1.9 A Thus, 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used, along with 5A MCCB breaker, to connect it to the EMDB.

## Slide 73
ESDB Diagram – Ground Floor

## Slide 74
ESDB Calculations – Ground Floor
ESDB_U:
Load = 0.7 x total emergency load = 0.7 x 800 = 560W Current = 560/(220 x 0.9) = 2.83 A Thus, 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used, along with 5A SP MCCB breaker, to connect it to the EMDB.

## Slide 75
ESDB Diagram – Single Unit

## Slide 76
ESDB Calculations – Single Unit
ESDB_U1:
For emergency condition, we will assume the power socket utility factor to be 0.2
Load = 0.7 x total emergency load + 0.2 x power socket load = 0.7 x 800 + 0.2 x 4000 = 1360W (1 Q socket is present on emergency) Current = 1360/(220 x 0.9) = 6.87 A Thus, 2 x 2.5 rm BYM cables and 2.5 rm BYA ECC cable has been used, along with 10A SP MCCB breaker, to connect it to the EMDB.

## Slide 77
ESDB Diagram – Double Unit – Unit 1

## Slide 78
ESDB Calculations – Double Unit – Unit 1
ESDB1_U2:
For emergency condition, we will assume the power socket utility factor to be 0.2
Load = 0.7 x total emergency load + 0.2 x power socket load = 0.7 x 540 + 0.2 x 4000 = 1178W (1 Q socket is present on emergency) Current = 1360/(220 x 0.9) = 5.95 A Thus, 2 x 2.5 rm BYM cables and 2.5 rm BYA ECC cable has been used, along with 10A SP MCCB breaker, to connect it to the EMDB.

## Slide 79
ESDB Diagram – Double Unit – Unit 2

## Slide 80
ESDB Calculations – Double Unit – Unit 1
ESDB2_U2:
For emergency condition, we will assume the power socket utility factor to be 0.2
Load = 0.7 x total emergency load + 0.2 x power socket load = 0.7 x 560 + 0.2 x 4000 = 1192W (1 Q socket is present on emergency) Current = 1192/(220 x 0.9) = 6.02 A Thus, 2 x 2.5 rm BYM cables and 2.5 rm BYA ECC cable has been used, along with 10A SP MCCB breaker, to connect it to the EMDB.

## Slide 81
ESDB Diagram – Roof

## Slide 82
ESDB Calculations – Roof
ESDB_R:
Load = 0.7 x total emergency load = 0.7 x 45 = 31.5W Current = 31.5/(220 x 0.9) = 0.159 A Thus, 2 x 1.5 rm BYM cables and 1.5 BYA ECC cable has been used, along with 5A SP MCCB breaker, to connect it to the EMDB.

## Slide 83
MDB and EMDB Diagrams

## Slide 84
Main Distribution Board Connection Diagram
40 kVA Generator

## Slide 85
MDB Calculations
The SDB loads are listed below: SDB_U = 616 W SDB_G = 728 W SDB1_1U = 8464 SDB1_2U = 6277 SDB2_2U = 6095 SDB_R = 175
Keeping in mind that 6 floors are dual units and 3 are single units, and we have installed extra Lift (18500 W) and pump (5000W), and utility factor = 0.7
Thus,
total MDB load = (SDB_U + SDB_G + SDB_R + 3x(SDB1_1U) + 6x(SDB1_2U + SDB2_2U) + Pump + Lift) x Utility Factor = 87.250 kW
As our Emergency system is not separate from the system supplied by the main, we don’t include EMDB loads in our MDB calculation, as it is already included.
Now,
I = P/3*V*PF = 146.89 A (V=220 V, pf = 0.9)
Thus, we will need 2x120 rm NYY + 120 rm BYA ECC wire and a 150 A SP MCCB Breaker.
S = P/pf = 96.944 kVA
We will need a 100kVA transformer substation.

## Slide 86
Others
PFI Plant
Here, Q = Ptan(cos-1(pf)) = 87.250 tan(cos-1(0.9)) = 42.257 KVAR
The PFI plant needs to deliver this much capacitive reactive power to bring the power factor close to unity.
Thus, current = Q/3*V*sin(cos-1(pf)) = 146.88 A
We need to use 2x120 rm NYY + 120 BYA ECC wires along with 150A SP MCCB breakers.
Elevator
Power = 18500 W Let, pf = 0.7 Thus, current = 18500 / 3*220*0.7 = 40.0432 A Thus, we need to use 2x25 rm NYY + 25 BYA ECC wires along with 50A SP MCCB breakers.
Pump
Power = 5000 W Let, pf = 0.7 Thus, current = 5000 / 3*220*0.7 = 10.823 A Thus, we need to use 2x4 rm NYY + 4 BYA ECC wires along with 15A SP MCCB breakers.

## Slide 87
Emergency Main Distribution Board Connection Diagram

## Slide 88
EMDB Calculations
The ESDB loads are listed below:
ESDB_U = 378 W ESDB_G = 560 W ESDB1_1U = 1360 ESDB1_2U = 1178 ESDB2_2U = 1192 ESDB_R = 31.5
total EMDB load = (ESDB_U + ESDB_G + ESDB_R + 3x(ESDB1_1U) + 6x(ESDB1_2U + ESDB2_2U) + Lift) x Utility Factor = 26.438 kW
Current
I = P/3*V*PF = 44.51 A (V=220 V, pf = 0.9)
Thus, we will need 2x25 rm NYY + 25 rm BYA ECC wire and a 50 A SP MCCB Breaker.
Apparent Power
S = P/pf = 29.38 kVA
Thus, a 40 kVA Generator is to be used.

## Slide 89
References

## Slide 90
Thank You for Your Patience